## DHW usage
DHW					Specific heat of water :	4.185	(kJ/kgC)	Jg-1C-1
		tank temp(C)	60				or	0.0011625	(Kwh/kgC)					3
		bath temp(C)	37			shower flow(l/m)		8		bath depth(cm)	15			2.0925
		shower temp(C)	42			shower time (m)		6		length(m)	1.35			10
		mains temp(C)	10					width(m)	0.54

		tot vol	HW vol	solar connected
	bath	98.4	53.1
	shower	48.0	30.7					Energy stored in tank down to:	50	C
	dishwasher	9.0	9.0	TRUE					(Kwh)
	washMC	56.0	39.2	TRUE					Tank temp
	handwash	1.0	0.5				tank size	60	40	60	80
				100	1.2	-1.2	1.2	3.5
Avg. Annual use			#people:	2			130	1.5	-1.5	1.5	4.5
	per person		household				160	1.9	-1.9	1.9	5.6
	#/day	#/wk	#/wk				190	2.2	-2.2	2.2	6.6
				usage(l)			220	2.6	-2.6	2.6	7.7
Bath		1		5,527			250	2.9	-2.9	2.9	8.7
shower	0.5		0	11,213			280	3.3	-3.3	3.3	9.8
dishwash			2	936			310	3.6	-3.6	3.6	10.8
washMC			1	2,038			340	4.0	-4.0	4.0	11.9
hands	2			730			370	4.3	-4.3	4.3	12.9
other(l)			10	0			400	4.7	-4.7	4.7	14.0
	l/d/person:	28.7137449438202		20,444			450	5.2	-5.2	5.2	15.7
			Kwh/yr	1,188			500	5.8	-5.8	5.8	17.4
			Kwh/day	3.3			600	7.0	-7.0	7.0	20.9
	Gas	6	p	71.3			700	8.1	-8.1	8.1	24.4
	Electric	11	p	130.7			800	9.3	-9.3	9.3	27.9
				900	10.5	-10.5	10.5	31.4
				1000	11.6	-11.6	11.6	34.9
				1500	17.4	-17.4	17.4	52.3
				2000	23.3	-23.3	23.3	69.8
				2500	29.1	-29.1	29.1	87.2
				3000	34.9	-34.9	34.9	104.6

## Monthly overview
Monthly Spread
Roof/Panel angle	30					Heating hours:	6
Panel size(tubes)	40		area:	2.9				Extra heating hours (work@home):	6

Stove output(KW)	4
HW output temp	50

(per month if not stated)	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	tots/avgs	gas cost	elec cost
Days away	0	14	2		14	4	14		2		2		52
Daytime working days	12	6	11	12	6	10	6	12	11	12	11	12	121
Heating hours/day	8.5	4.5	7.9	8.5	4.5	0.0	0.0	0.0	7.9	8.5	7.9	8.5	5.5
Heating hours	254.5	134.5	236.5	254.5	134.5	0	0	0	236.5	254.5	236.5	254.5	1997

Solar:
Insolation (Kwh/m2/day)	0.64	1.17	1.94	3.22	4.17	5	4.44	3.61	2.78	1.67	0.78	0.47	29.89
(from panelangle sheet (Kwh/m2/day)	0.9	2.9	2.9	2.9	4.54	4.54	4.54	2.9	2.9	2.9	0.9	0.9	33.72
Heat to panel (Kwh/day)	1.856	3.393	5.626	9.338	12.093	14.5	12.876	10.469	8.062	4.843	2.262	1.363
Heat to panel (Kwh)	79.3875	103.20375	171.124166666667	284.030833333333	367.82875	441.041666666667	391.645	318.432083333333	245.219166666667	147.307916666667	68.8025	41.4579166666667	2,659	160	293

DHW usage (l)	1703.6822	919.521625753425	1591.65926082192	1703.6822	919.521625753425	1479.63632164384	919.521625753425	1703.6822	1591.65926082192	1703.6822	1591.65926082192	1703.6822	17,532
Mains water incoming temp (C)	4	5	7	9	12	14	15	14	12	9	7	5	9.4
Water Heating requirement (Kwh)	91.104405645	48.102475047226	79.5630673003356	81.2017528575	40.6198678176575	61.9227800607945	37.4130361478425	71.29910007	70.3115478468082	81.2017528575	79.5630673003356	89.1238750875	831	50	91

Avg outside temp (Cam, 2006. C)	4	3.8	4.7	9.1	13.1	17.9	21.6	17.1	18	13.7	8	6.3	11
Space Heating avg power(whole house) (Kw)	3.9	4	3.7	2.8	2	1	0.3	1.1	0.9	1.8	3	3.3	2.3
Space Heating requirement (kwh)	993	538	875	713	269	0	0	0	213	458	710	840	5,608	336	617
Space Heating avg power (lounge)(Kw)	2.3	2.3	2.3	1.9	1.2	0.3	0	0.4	0.3	1.1	2	2.1
Space Heating requirement (kwh)	585	309	544	484	161	0	0	0	71	280	473	534	3,442	207	379

Stove hours (per day)	6.0	4.5	6.0	6.0	4.5	0.0	0.0	0.0	6.0	6.0	6.0	6.0
Solar provided (Kwh)	64	83	137	227	294	353	313	255	196	118	55	33	2,128	128	234
Solar useable (Kwh)	64	83	137	227	294	62	37	71	196	118	55	33	1,377	83	152
Solar fraction for DHW	0.7	1.7	1.7	2.8	7.2	5.7	8.4	3.6	2.8	1.5	0.7	0.4
Solar space heating (Kwh)	0	34	57	146	254	291	276	183	126	37	0	0	1,404	84	154
Solar space heating useable (Kwh)	0	34	57	146	161	0	0	0	71	37	0	0	507	30	56
Stove provided (Kwh)	730	294	682	730	294	0	0	0	682	730	682	730	5,555	333	611
Stove fraction for heating	1	1	1	1	1				3	2	1	1
Boiler Provided (Kwh)	290	209	136	0	0	0	0	0	0	0	52	166	853	51	94
Solar fraction for heating	0.0	0.1	0.1	0.2	0.9				0.6	0.1	0.0	0.0	0.2
Heat to dump (Kwh)	0.0	0.0	0.0	0.0	0.0	15.0	92.5	57.6	89.2	36.6	0.0	0.0

## CH heatloss
				u-values (W/m2.K)
				now	pre-insul	window factor		0.17
Whole house approximation					wall(cavityfill)	0.45	1.71	avg air changes		1.2
				house wall (IWI)	0.148	0.45
				window	2	2	specific heat factor		0.33	1.05 x 1000 x ? /3600
				ext door	1.4	4
				ceiling	0.16	0.5
Size					floor	1.2	1.2		Floor calcs (US ‘3ft perimeter’)
	Internal	External	windows	across	up			int wall	1.9			area overall	54.6	m2
length(m)	8.22	8.83	north down					int door	5			perimeter width	0.9	m
width(m)	6.64	7.26	south down					bay roof	0.12	4		perimeter area	23.5	m2
height(m)	2.4	5	north up					1st floor	2			central area	31.1	m2
floors	2		south up					solidwall+fill	1.85
				single-glazed window	5			Floor calcs (BRE IP3/90)
	Area(m2)	temp diff	Heat loss(W/m2)	(pre-insul)				between floors	2.081			area overall	54.6	m2
Wall	142.7	21	4252	368				50mm PUR on inside	0.23			perimeter	16.4	m2
Window	24.3	21	1019	1019				75mm PUR inside	0.19			P/A ratio	0.30	m-1
Floor	54.6	9	928	336	565			3G window	0.72			U	0.49	W/m2K
Roof (ceiling)	54.6	21	573	573	heatloss			sunroom wall	0.135
total(W/K)			6772	2295				garage walls	0.200			Floor calcs (CIBSE Guide A3)
	vol (m3)					block+block doorwall	0.270
ventilation	261.98784	21	4357	654		range(Kwh)	5240	EWI150mmEPS	0.14
				2949			13099
			11129	W	11.1	kW			imperial/metric conversion:	0.14422	(btu.in/hf.F.ft2 -> W/mK)
				Material	k(btu.in/ hr.F.ft2)	k (W/mK)	R(1/k) (imperial)	R(1/k) (mK/W)
				As built:	1.71				polystyrene (cut edge)	0.25	0.038	4.00	26.32
U-values				Cavity fill:	0.45				polystyrene(smooth surface)	0.2	0.028844	5.00	34.67
house wall (IWI)	k (W/mK)	thickness(m)	R(m2K/W)	plus therm bd:	0.15				brick (outer leaf)	9	0.84	0.11	1.19
PUR thermal bd	0.022	0.1	4.55					brick (inner leaf)		0.62		1.61
inside surface			0.13	0.13					plasterboard	4.5	0.21	0.22	4.76
plaster	0.21	0.018	0.09	0.09			264.6		mortar (inner leaf)		0.88		1.14
brick	0.62	0.102	0.16	0.16					mortar (outer leaf)		0.94		1.06
rockwool	0.04	0.065	1.63	0.00					rockwool		0.04		25.00
brick	0.62	0.102	0.16	0.16					phenolic foam		0.022		45.45
outside			0.04	0.04					fibreboard		0.1		10.00
		0.287	0.148	1.71	11.55	improvement factor			dritherm32		0.032		31.25
				multipro		0.26
				Cavity fill:	0.45				7kN concrete block		0.19
house wall (EWI160)	k (W/mK)	thickness(m)	R(m2K/W)	plus EWI:	0.16				celcon block		0.11
inside surface			0.13					softwood		0.13
plaster	0.21	0.018	0.09					rockwool, blown		0.04
brick	0.62	0.102	0.16					glasswool		0.04
rockwool	0.04	0.065	1.63					Platinum EPS		0.031
brick	0.62	0.102	0.16					Hardwood		0.18
				Extruded poly		0.033
Uditherm	0.039	0.12	3.08					Cosywool (ty mawr)		0.036
Uditherm hard bit	0.049	0.04	0.82					leca		0.1
render	0.21	0.018	0.09					plaster		0.32
outside			0.04					karndean		0.4
		0.345	0.165					linleum		0.25
				screedboard		0.4
Bay roof	k (W/mK)	thickness(m)	R(m2K/W)					belthermo woodfibre		0.037
outside			0.04	0.04					Pavatex woodfibre		0.043
felt	1	0.002	0.00	0.00					Acrylic render		1
plank	0.12	0.012	0.10	0.10					screed		1.4
fibreboard	0.1	0.018	0.00	0.18					concrete slab		2
kingspan	0.022	0.050	2.27					cw2000 cemwood		0.075
glasswool	0.04	0.130	3.25	0.04	(air gap)				litho
polystyrene	0.038	0.100	2.63	0.00
plasterboard	0.21	0.0095	0.05	0.05
inside			0.10	0.10
			0.118	1.956	16.5	improvement factor

Garage Wall	k (W/mK)	thickness(m)	R(m2K/W)
inside			0.13	0.13
multipro 9mm	0.26	0.009	0.03	0
recticel PIR+timber	0.022	0.05	2.27	0				Air-gaps			m2K/W
Recticel PIR	0.022	0.05	2.27	0					cavity		0.18
brick	0.84	0.2	0.24	0.24					external surface (wall)		0.04
outside			0.04					internal surface (wall)		0.13
			0.200	2.717	13.55	improvement factor			external surface (roof)		0.04
				internal surface (roof)		0.10
Garage door	outer frame	0.05	break width	0.03					external surface (floor)		0.04
	doorframing	0.1					internal surface (floor)		0.17
	width	2.1	area	4.2
	height	2			total	local
	Cond(W/mk)	thickness	Rest(m2K/W)	Area (m2)	Area fraction	area fraction	layer
outside			0.04
Timber facing	0.15	0.05	0.33	3.9	0.93	1.00	1a
PIR	0.022	0.1	4.55	2.76	0.66	0.71	2a
ply	0.18	0.025	0.14	3.9	0.93		3a				area	Rupper	Rlower
Door frame	0.15	0.1	0.67	1.14	0.27	0.29	2b		doorframepath res	1.31	0.29
outer frame	0.15	0.15	1.00	0.295	0.07	1.00	4,6		doorinspath res	5.19	0.71	2.78
frame break	0.15	0.05	0.33	0.122	0.03	0.41	5a		sharedpath	0.64
outerframe@break	0.15	0.05	0.33	0.173	0.04	0.59	5b		bridgedpath	1.68			2.33
inside			0.13				Rmax	Rmin	Ravg		totalres	2.55
			doornom	0.19	Udoor:	0.39	2.78	2.33	2.55		U=	0.39
Max U (BS6946)					Uframe:	0.60	1.82	1.50	1.66
				Utot	0.41	2.46	2.46	2.46

Block+Block wall
inside			0.13
plaster	0.21	0.02	0.10
thermal block	0.11	0.1	0.91
Rockwool	0.04	0.065	1.63
thermal block	0.11	0.1	0.91
outside			0.04
			0.270
Extension Wall
inside			0.13
plaster	0.21	0.02	0.10
block (dense)	0.19	0.1	0.53
Dritherm 32	0.032	0.2	6.25
brick	0.26	0.1	0.38
outside			0.04
			0.135
Gnd floor ceiling
below			0.10
plasterboard	0.21	0.01	0.05
gap		0.18	0.14	0.12
joist	0.13	0.18	1.38	0.15
floorboard	0.13	0.02	0.15
above			0.04
				2.081

				As built:	1.80
				Cavity fill:	0.46
house wall (EPS)	k (W/mK)	width(m)	R(m2K/W)	plus EWI:	0.14
inside surface			0.13	0.13
plaster	0.32	0.018	0.06	0.06
brick	0.62	0.102	0.16	0.16
rockwool	0.04	0.065	1.63	1.63
brick	0.62	0.102	0.16	0.16
platinum EPS	0.03	0.150	5.00	5.00	improvement
outside			0.04	0.04	factor:
		0.437	0.139	0.139	12.9

Thermal Mass
From SAP:	19	(Thermal Mass Parameter) Solid floor. Masonry+dense plaster on all walls
floor	Y(W/m2K)			Thermal mass= Sum(area, addmittance(Y))/total floor area
concrete,carpet	3.2

Heatloss room by room					Total:	4059.64623528331	7479.88564305997
				Inc outerrooms:	6932.56338985031	10352.802797627
Target temps
room	temp	air changes
lounge	20	1.5
kitchen	17	2					Height of cavity blocked with crap (m)	0.4
hall	14	2
bog	18	1
bedroom	16	1
wookoffice	20	1.5
tessoffice	20	1.5
bathroom	23	2
unusedroom	10
unusedouterroom	8
workshop	18	2
airing cupboard	25	0.5
pottingshed	12	1
sunroom	20	1.5

Ground temp	11
outside design temp	-1
Ventilation temp	-1

Lounge		Tempdiff			heatloss		total
element	Area	(wholehouse)	(roomonly)	U-value	(wholehouse)	(roomonly)
External wall	15.2	21	21	0.15	47	47
Sunroom wall	7.3	0	12	0.45	0	40
External wall foot	4.8	21	21	1.71	173	173	220	220
Bay window	6.6	21	21	0.72	99	99
Window	2.3	21	21	0.72	34	34
ext glass door	1.8	0	12	2	0	44
kitchen wall	7.5	3	10	1.9	43	142
hall wall	12.0	6	10	1.9	136	227
floor	32.9	9	9	1.2	355	355
Ceiling (office)	13.3	0	10	2	0	267
Ceiling (to bed)	18.3	4	10	2.08	152	381
Bay window ceil	1.6	21	21	0.12	4	4
	vol			coeff	1043	1812	whole	roomonly
ventilation	78.9	21	21	0.495	821	821	1864	2633
				1208	1976
wookoffice
External wall(S)	6.083	21	21	0.15	19	19
External wall(W)	7.635	21	21	0.15	24	24	43	43
Window(S)	1.1128	21	21	0.72	17	17
Window(W)	1.1128	21	21	0.72	17	17
Door	1.4504	6	6	2	17	17
T-office wall	4.3204	0	10	1.9	0	82
Bed wall	8.7478	4	10	1.9	66	166
Ceiling	14.1856	21	21	0.16	48	48
floor	14.1856	0	10	2	0	284
	vol			coeff	208	673	whole	roomonly
ventilation	32.6	21	21	0.495	339	339	547	1013
				276	741
tessoffice
External wall(N)	5.0652	21	21	0.15	16	16
External wall(W)	5.1618	21	21	0.15	16	16	32	32
Window(W)	1.1128	21	21	0.72	17	17
W-office wall	4.3204	0	10	1.9	0	82
Hall wall	5.496	0	10	1.9	0	104
Ceiling	7.1666	21	21	0.16	24	24
floor	7.1666	0	10	2	0	143
	vol			coeff	73	403	whole	roomonly
ventilation	16.5	21	21	0.495	171	171	244	574
				107	437
Bedroom
External wall(S)	6.825	17	17	0.148	17	17
External wall(E)	8.7478	17	17	0.148	22	22	39	39
Window	2.3004	17	17	0.72	28	28
W-office wall	9.8928	-4	6	1.9	-75	113
Bathroom wall	3.9617	-7	6	1.9	-53	45
Hall wall	2.29	2	6	1.9	9	26
Airing cupboard	2.29	-9	6	1.9	-39	26
Ceiling	17.8528	17	17	0.16	49	49
Floor	17.8528	-4	6	2	-143	214
	vol			coeff	-185	540	whole	roomonly
ventilation	41.1	17	17	0.33	230	230	45	771
				-139	586
Bathroom
External wall(N)	3.9524	24	24	0.15	14	14
External wall(W)	6.2746	24	24	0.148	22	22	36	36
Window	1.1128	24	24	0.72	19	19
Bedroom wall	2.29	7	13	1.9	30	57
Hall wall	5.496	9	13	1.9	94	136
Ceiling	7.1666	24	24	0.16	28	28
Floor	7.1666	6	13	2	86	186
	vol			coeff	294	462	whole	roomonly
ventilation	16.5	24	24	0.66	261	261	555	723
				346	514
Kitchen
External wall(N)	6.9787	18	18	0.15	19	19
External wall foot(N)	1.736	18	18	0.19	6	6
External wall(W)	5.42	-3	9	0.45	-7	22
External wall foot(W)	1.084	-3	9	1.85	-6	18
Window	1.7013	18	18	0.72	22	22

Door	2.2684	9	9	4	82	82
Lounge wall	8.616	-3	7	1.9	-49	115
Hall wall	6.504	3	7	1.9	37	87
Ceiling	10.2701	-6	7	2.081	-128	150
Floor	10.2701	6	6	1.2	74	74
	vol			coeff	49	593	whole	roomonly
ventilation	24.6	18	18	0.66	293	293	341	886
				107	652
Hall/Bog
External wall(N)	11.9994	15	15	0.14	25	25
External wall foot(N)	1.816	15	15	0.14	4	4
External wall(E)	3.4616	19	15	0.14	9	7
External wall foot(E)	1.084	19	15	0.14	3	2	41	38
Window	1.1128	19	15	0.72	15	12
Window	1.1128	15	15	0.72	12	12
Ext Door	1.9584	15	15	1.6	47	47
Lounge wall	10.848	-6	4	1.9	-124	82
Kitchen wall	5.352	-3	4	1.9	-31	41
Ceiling(t-office)	7.046	-6	4	2.081	-88	59
Ceiling(Loft)	6.0836	15	15	0.160	15	15
Floor	10.17	3	3	1.2	37	37
	vol			coeff	-76	342	whole	roomonly
ventilation	54.5	15	15	0.66	539	539	464	882
				32	450

Workshop
Outside Wall	8	19	19	0.200	30	30
End (outside) wall	1.75	19	19	0.200	7	7
Party Wall	15.588	19	19	0.200	59	59
Roof Windows	1.2	19	19	2	46	46
Garage Door	4.21875	19	19	0.5	40	40
Door	2.1	6	10	1.9	24	40
Roof	14.5	19	19	1.9	523	523
Pottingshed wall	6.399	6	10	1.9	73	122
Floor	14.5	7	7	0.3	30	30
	vol			coeff	833	898	whole	roomonly
ventilation	39.73	19	19	0.66	498	498	1331	1396
				933	997

Sunroom
Outside Wall (glazed)	5.75775	21	21	1.1	133	133
Outside wall (E)	9.2	21	21	0.200	39	39
Glazing	10.82725	21	21	0.9	205	205	338	338
Floor	27.02	9	9	0.15	36	36
Front Door	2.31	21	21	1.3	63	63
Roof	32.08	21	21	0.16	108	108
Pottingshed wall	10.68	8	12	1.9	162	244
Pottingshed door	2.1	8	12	1.9	32	48
Workshop door	2.1	8	12	1.9	32	48
Lounge wall	9.741	0	10	0.45	0	44
Kitchen wall	7.5735	3	10	0.45	10	34
Bedroom wall	4.8132	4	10	0.45	9	22
Bathroom wall	1.2222	-3	10	0.45	-2	6
	vol			coeff	827	1029	whole	roomonly
ventilation	73.1	19	19	0.495	688	688	1515	1716
				965	1166

Pottingshed
Window	1.1	13	13	5	72	72
Party Wall	12.2539	13	13	0.200	32	32
Roof Window	0.6	13	13	2	16	16
Door	2.1	-8	2	1.9	-32	8
Roof	16	13	13	0.16	33	33
Workshop wall	6.399	-6	4	1.9	-73	49
Sunroom wall	10.68	-8	4	1.9	-162	81
Floor	7.42	1	1	0.3	2	2
	vol			coeff	-113	292	whole	roomonly
ventilation	22.26	19	19	0.33	140	140	27	432
				-85	320

## Tank Losses
Tank losses		heat loss coefficient for storage tank:				0.1429	Btu/hr*ft2*F

Manufacturer		Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron
Tank volume (l)		120	135	172	210	144	168	216	259	320	450
Tank height (mm)		1050	1200	1500	1800	1050	1200	1500	1800	1800	1800
Tank Diameter (mm)		400	400	400	400	450	450	450	450	500	550
Insulation thickness (mm)		75	75	75	75	75	75	75	75
Surface area (m2)		1.57	1.76	2.14	2.51	1.80	2.01	2.44	2.86	3.22	3.58
k-value (W/mK)		0.02	0.02	0.02	0.02	0.02	0.02	0.02	0.02
R-value (K.m2/W)		3.75	3.75	3.75	3.75	3.75	3.75	3.75	3.75	3.75	3.75
U-value (W/K.m2)		0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27
Heat loss (W) @ temp diff	90	38
	80	34	38	46	54	38	43	52	61	69	76
	70	29	33	40	47	34	38	46	53	60	67
	60	25	28	34	40	29	32	39	46	52	57
	50	21	23	28	34	24	27	33	38	43	48
	40	17	19	23	27	19	21	26	31	34	38
	30	13	14	17	20	14	16	20	23	26	29
	20	8	9	11	13	10	11	13	15	17	19
	10	4	5	6	7	5	5	7	8	9	10

Heatloss (kWh) @50Cdiff,hrs	12	0.25	0.28	0.34	0.40	0.29	0.32	0.39	0.46	0.52	0.57
	24	0.50	0.56	0.68	0.80	0.58	0.64	0.78	0.92	1.03	1.15
From newark sheet (50mm)	24	1.3	1.39	1.6	1.8	1.45	1.58	1.84	2.05	2.34

			Tank energy input:
			From	to	diff	vol	energy
		top	28	65	37	20	0.86
		tank4	27	57	30	20	0.70
		tank3	26	63	37	20	0.86
		tank2	25	57	32	20	0.74
		bottom	23	44	21	20	0.49
							3.65

## Gas-n-Leccy Usage
Current Usage
Leccy	Leccy
				Meter 1	read/estimated			Meter 2	read/estimated					price for		price		Kwh/day	£/day
Billdate	From	to	period	start		end		start		end		Meter1	Meter2	Total	1st		(rest)	cost
			(days)	(Kwh)		(Kwh)		(Kwh)		(Kwh)		Kwh	Kwh	Kwh	(pence)	Kwh	pence	£

					1480.83187172846	=
		2007-05-21				2647	r			6920	r
2007-08-17	2007-05-21	2007-08-17	88	2647	r	2731	r	6920	r	7126	r	84	206	290	11.066	217	7.975	29.83497	3.29545454545455	0.33903375
	2007-08-17	2007-11-19	94	2731	r	2870	r	7126	r	7474	r	139	348	487	11.066	232	7.975	46.00937	5.18085106382979	0.489461382978723
2008-03-04	2007-11-19	2008-01-17	59	2870	r	2931	e	7474	r	7631	e	61	157	218	11.066	146	7.975	21.89836	3.69491525423729	0.371158644067797
	2008-01-17	2008-01-28	11	2931	e	2943		7631	e	7660		12	29	41	17.878	15	9.35	5.1127	3.72727272727273	0.464790909090909

	Gas
	Pay first rate on	12.526	kWh/day					magic
Measured		2007-01-12					calories	factor	4180.9	(annual total 2007)			110.939731075822
	2007-01-12	2007-01-27	15	6033		6059	r					39.251	31.5542190753333	820.4	3.56	188	2.732	23.97	56.80	1.60
	2007-01-27	2007-02-04	8	6059		6064	r					39.251	31.5542190753333	157.8	2.979	100	2.192	4.25	23.67	0.53
	2007-02-04	2007-02-11	7	6064		6068	r					39.251	31.5542190753333	126.2	2.979	88	2.192	3.46	22.54	0.49
	2007-02-11	2007-02-24	13	6068		6071	r					39.251	31.5542190753333	94.7	2.979	163	2.192	2.82	9.71	0.22
	2007-02-24	2007-03-11	15	6071		6074.2	r					39.251	31.5542190753333	101.0	2.979	188	2.192	3.01	8.84	0.20
	2007-03-11	2007-05-03	53	6074.2		6075.6	r					39.251	31.5542190753333	44.2	2.979	664	2.192	1.32	1.43	0.02
	2007-05-03	2007-06-30	58	6075.6		6075.9	r					39.251	31.5542190753333	9.5	2.979	727	2.192	0.28	0.71	0.00
	2007-06-30	2007-09-30	92	6075.9		6076.8	r					39.251	31.5542190753333	28.4	2.979	1152	2.192	0.85	0.65	0.01
	2007-09-30	2007-10-05	5	6076.8		6080.7	r					39.251	31.5542190753333	123.1	2.979	63	2.192	3.19	30.92	0.64
	2007-10-05	2007-10-12	7	6080.7		6085.5	r					39.251	31.5542190753333	151.5	2.979	88	2.192	4.01	26.14	0.57
	2007-10-12	2007-10-19	7	6085.5		6090.5	r					39.251	31.5542190753333	157.8	2.979	88	2.192	4.15	27.05	0.59
	2007-10-19	2007-10-24	5	6090.5		6095.3	r					39.251	31.5542190753333	151.5	2.979	63	2.192	3.82	36.60	0.76
	2007-10-24	2007-10-31	7	6095.3		6102.6	r					39.251	31.5542190753333	230.3	2.979	88	2.192	5.74	37.41	0.82
	2007-10-31	2007-11-07	7	6102.6		6110.9	r					39.251	31.5542190753333	261.9	2.979	88	2.192	6.43	41.92	0.92
	2007-11-07	2007-11-14	7	6110.9		6119.7	r					39.251	31.5542190753333	277.7	2.979	88	2.192	6.78	44.18	0.97
	2007-11-14	2007-11-23	9	6119.7		6129.8	r					39.251	31.5542190753333	318.7	2.979	113	2.192	7.88	38.92	0.88
	2007-11-23	2007-12-10	17	6129.8		6146.9	r					39.251	31.5542190753333	539.6	2.979	213	2.192	13.50	33.60	0.79
	2007-12-10	2007-12-18	8	6146.9		6154.5	r					39.251	31.5542190753333	239.8	2.979	100	2.192	6.04	33.92	0.76
	2007-12-18	2008-01-07	20	6154.5		6159.1	r					39.251	31.5542190753333	145.1	2.979	251	2.192	4.32	8.84	0.22
	2008-01-07	2008-01-14	7	6159.1		6165.5	r					39.251	31.5542190753333	201.9	2.979	88	2.192	5.12	33.36	0.73

Gas					1177
					price for		price for
Bills		2007-01-12				6033	r					calories		4151.8603489882	1st	Kwh	rest	119.13
	2007-01-12	2007-01-15	3	6033	r	6035	e					39.21	31.520052957	63.0	4.959	38	2.801	2.59	21.0	0.86
	2007-01-15	2007-02-15	31	6035	e	6069	r					39.21	31.520052957	1071.7	3.56	401	2.732	32.60	34.6	1.05
	2007-02-15	2007-05-21	95	6069	r	6075	r					39.25	31.5551837657333	189.3	2.979	1190	2.192	5.64	2.0	0.06
	2007-05-21	2007-08-07	78	6075	r	6076	r					39.25	31.5551837657333	31.6	2.979	977	2.192	0.94	0.4	0.01
	2007-08-07	2007-11-19	104	6076	r	6124	r					39.25	31.5542190753333	1514.6	2.979	1303	2.192	43.45	14.6	0.42
	2007-11-19	2008-01-17	59	6124	r	6165	r					38.88	31.2597473307333	1281.6	2.979	739	2.192	33.91	21.7	0.57
	2008-01-18	2008-02-08	21	6165	r	6175	r					38.88	31.2597473307333	312.6	5.49	263	2.302	15.58	14.9	0.74
	2008-02-08			6175	r

					4174.62318366661	(annual total 2007)		110.801397379395
					1028.66754185585	(annual total 2008)		28.9431424454511
					186.169892544455	(annual total 2009)		4.87848281611855

Measured		2007-01-12
	2007-01-12	2007-01-27	15	6033		6059	r					820.409695958667	3.56	188	2.732	23.97	54.7	1.60
	2007-01-27	2007-02-04	8	6059		6064	r					157.771095376667	2.979	100	2.192	4.25	19.7	0.53	Installed wood-burner
	2007-02-04	2007-02-11	7	6064		6068	r					126.216876301333	2.979	88	2.192	3.46	18.0	0.49
	2007-02-11	2007-02-24	13	6068		6071	r					94.662657226	2.979	163	2.192	2.82	7.3	0.22
	2007-02-24	2007-03-11	15	6071		6074.2	r					100.973501041061	2.979	188	2.192	3.01	6.7	0.20	Pilot light turned off
	2007-03-11	2007-05-03	53	6074.2		6075.6	r					44.1759067054839	2.979	664	2.192	1.32	0.8	0.02
	2007-05-03	2007-06-30	58	6075.6		6075.9	r					9.46626572257704	2.979	727	2.192	0.28	0.2	0.00
	2007-06-30	2007-09-30	92	6075.9		6076.8	r					28.3987971678172	2.979	1152	2.192	0.85	0.3	0.01
	2007-09-30	2007-10-05	5	6076.8		6080.7	r					123.061454393789	2.979	63	2.192	3.19	24.6	0.64	Gunde Arrived - heating turned on
	2007-10-05	2007-10-12	7	6080.7		6085.5	r					151.460251561606	2.979	88	2.192	4.01	21.6	0.57
	2007-10-12	2007-10-19	7	6085.5		6090.5	r					157.771095376667	2.979	88	2.192	4.15	22.5	0.59
	2007-10-19	2007-10-24	5	6090.5		6095.3	r					151.460251561606	2.979	63	2.192	3.82	30.3	0.76
	2007-10-24	2007-10-31	7	6095.3		6102.6	r					230.345799249939	2.979	88	2.192	5.74	32.9	0.82
	2007-10-31	2007-11-07	7	6102.6		6110.9	r					261.900018325244	2.979	88	2.192	6.43	37.4	0.92
	2007-11-07	2007-11-14	7	6110.9		6119.7	r					277.677127862939	2.979	88	2.192	6.78	39.7	0.97
	2007-11-14	2007-11-23	9	6119.7		6129.8	r					318.697612660878	2.979	113	2.192	7.88	35.4	0.88	Gunde Left
	2007-11-23	2007-12-10	17	6129.8		6146.9	r					539.577146188183	2.979	213	2.192	13.50	31.7	0.79
	2007-12-10	2007-12-18	8	6146.9		6154.5	r					239.812064972545	2.979	100	2.192	6.04	30.0	0.76
	2007-12-18	2008-01-07	20	6154.5		6159.1	r					145.149407746545	2.979	251	2.192	4.32	7.3	0.22	New boiler working 2007-12-21
	2008-01-07	2008-01-14	7	6159.1		6165.3	r					195.636158267061	2.979	88	2.192	4.98	27.9	0.71	No woodburner - 2days all-day heating
	2008-01-14	2008-01-22	8	6165.3		6168	r					85.1963915033943	2.979	100	2.192	2.54	10.6	0.32
	2008-01-22	2008-03-28	66	6168		6176.8	r					277.677127862939	2.979	827	2.192	8.27	4.2	0.13
	2008-03-28	2008-04-06	9	6176.8		6176.8	r					0	2.979	113	2.192	0.00	0.0	0.00
	2008-04-06	2008-07-20	105	6176.8		6181	r					132.527720116394	2.979	1315	2.192	3.95	1.3	0.04
	2008-07-20	2008-09-24	66	6181		6181	r					0	2.979	827	2.192	0.00	0.0	0.00
	2008-09-24	2008-12-04	71	6181		6183.2	r					69.4192819657276	2.979	889	2.192	2.07	1.0	0.03
	2008-12-04	2008-12-10	6	6183.2		6184.4	r					37.8650628903943	2.979	75	2.192	1.13	6.3	0.19
	2008-12-10	2008-12-10	0	6184.4		6185.15	r					23.6656643065	2.979	0	2.192	0.52	#DIV/0!	#DIV/0!
	2008-12-10	2008-12-28	18	6185.15		6186	r					26.8210862140448	2.979	225	2.192	0.80	1.5	0.04
	2008-12-28	2009-01-09	12	6186		6188.6	r					82.0409695958782	2.979	150	2.192	2.44	6.8	0.20	On 12hrs for thermal survey
	2009-01-09	2009-01-10	1	6188.6		6191.7	r					97.8180791335161	2.979	13	2.192	2.25	97.8	2.25
	2009-01-10	2009-07-02	173	6191.7		6194.5	r					88.3518134109391	2.979	2167	2.192	2.63	0.5	0.02
	2009-07-02					0	2.979	0	2.192	0.00	#DIV/0!	#DIV/0!

## UFH
Total pipe length	100
Pressure drop in pipes

Independent heating, old fashioned ventilation				Uncoverd
	Max power needed	Area		area
	W	m2	W/m2	m2	W/m2
Workshop	1396	13.2	106	7	199
Sunroom	1716	27	64
Lounge	2633	32.1	82
Kitchen	886	10.2	87	5	=
Bog	882	7.07	125
Wook office	1013	12.9	78
Bathroom	723	4.3	168
Tess office
Bedroom
Hall+Landing

Independent heating, controlled ventilation
	Max power needed	Area
	W	m2	W/m2
Workshop	997	13.2	75.5
Sunroom	1166	27	43.2
Lounge	1976	32.1	61.6
Kitchen	107	10.2	10.5
Bog	450	=	#VALUE!
Wook office	741	12.9	57.5
Bathroom	514	4.3	119.5
Tess office			#DIV/0!
Bedroom			#DIV/0!
Hall+Landing			#DIV/0!

insulation full thickness Sh (m)	0.06
insulation min thickness Sl (m)	0.043
pipe spacing T (m)	0.12
pipe diameter D (m)	0.016
eff. Insulation thickness, Sins (m)	0.058
						Exernal design temp			C	0	-5	-15
Insulating layer therm res Rl,ins (m2K/W)	1.604	(sins/lins)	OK			Required insulation resistance			m2K/W	1.25	1.5	2
Insulation conductivity lins(W/mK)	0.036
External design temp	-5	Can be 0, -5 or -15

Design value qdes	75.5	heat load/surf area
heat Load Qn,f	997
Heating surface area Af (m2)	13.2

heat output Qf (W)	660	q * area
specific thermal output q	50

	output	operating temp
	W/m2	C
lithotherm	50	27	(for stone/ceramic floor, 180mm pipe spacing, 20C room)
	60		(for stone/ceramic floor, 90mm pipe spacing, 20C room)

Floor options	R-value	U-value	thermal conductivity up		cost/m2

XPS+screedboard+LVT
PUR+screedboard
TF70+screedboard
cemwood+lithoboard
XPS+concrete
XPS+anhydrite

## BOM
		Parts, prices, suppliers					coil	cost/m2				PHE for water+solar	PHE for DHW only
		DHW simple					2129					1937	2056
		Solar Circuit, 20 tubes					627					669	627
		Tank+DHW					758					524	685
		Boiler					744					744	744

		DHW simple					2225					2256	2375
		Solar Circuit, 40 tubes					947					989	947
		Tank+DHW					534					524	685
		Boiler					744					744	744

		DHW+heating, vented										2560	2601
		Solar Circuit, 40 tubes										989	947
		Tank+DHW										827	911
		Boiler										744	744

		DHW+heating, vented, DPS	DPS: solar coil, inc anti-vacum, strainer										3200
		Solar Circuit, 40 tubes											947
		Tank+DHW											1510
		Boiler											744

		DHW+heating, combi										2795
		Solar Circuit, 40 tubes										989
		Tank+DHW										885
		Boiler										921

		DHW+heating, combi, DPS											3026
		Solar Circuit, 40 tubes											947
		Tank+DHW											1159
		Boiler											921

ref		item	spec	size	#items	supplier	price	cost/m2				part number	Manufacturer	URL	Datasheet/info

Solar		20 tube 47mm panel				navitron	395
		fitting kit				navitron	9.5
	.	20 tube 47mm panel				eco-nomical	319.6					47-1500-20	chinese	http://eco-nomical.co.uk/SolarWaterProduct.htm
	.	fitting straps, stainless	9mm holes			eco-nomical	11.08
		10mm tube	35m coil			BES	41.83					6941		http://www.bes.co.uk/products/139.asp
		10mm tube	10m coil			navitron
	.	10mm tube	25m coil			screwfix	36
	.	HT armaflex 10mm	10m			navitron	30.5
	.	Expansion tank	18l			eco-nomical	36.72						Zilmet
	.	Exp tank fitting kit	bracket, 500mm stainless flex (3/4"BSP F, QR valve			eco-nomical	22.03
		Antifreeze 5l	5l			Navitron	22					+ £21 delivery
		Antifreeze 5l	5l			eco-nomical	17.63
		High temp air bleed valve	3/8" BSP M, F			eco-nomical	29.38
		pump 12V 1.3A Craig	Brushless,20mm OD spigot			ebay - easy_flow_pumps	64					inc £4 delivery and £5connectors	Daviescraig	http://myworld.ebay.co.uk/easy_flow_pumps/	http://www.daviescraig.com.au/main/display.asp?pid=27
		12V supply				ebay - imikhan786	13							http://search.ebay.co.uk/_W0QQsassZimikhan786
		Filler (modified sprayer)				eco-nomical	25.56
	.	Filler (modified sprayer)				navitron	25
	.	Fill/drain valves	15mm OD barbs 1/2" BSP F 3/4" BSP M			eco-nomical	29.28
		Pressurised kit					69					88.03
		20mmrubber/10mm brass fittings
	.	PHE	Vaillant			ebay	40
		PHE	Vaillant 06-4950			abotuk.co.uk	46.87075					HE113	Vaillant	http://abcotuk.co.uk/Product.asp?ProductId=P217&Catid=C2
		PHE	Vaillant			abotuk.co.uk	34.385					HE110
	.	PHE fittings	15mm elbow*2+Tee				7.97825
		3-way valve	3-way, 22mm			hav.co.uk	63.48					honeywell
		Zone valve	2-way 22mm			honeywell	45					honeywell
		3-way valve	3-way, 22mm			ebay	40
		Zone valve	2-way 22mm			ebay	30
		Zone valve	2-way 22mm			abcot uk	26.9075						ORKLI	http://www.abcotuk.co.uk/Product.asp?ProductId=P536&Catid=C2
		3-way valve				abcot uk
		solenoid valve				hav.co.uk	45
		Anti-scale device					50

Tank		tank 123l twin coil	1050*400, 75mm insul			navitron	428
		123l thermal store, twin coil	inc expansion vessel, mixervalve			navitron	758
		tank 210l, twin coil	1800x400,75mminsul			navitron	498
		210l thermal store, twin coil	inc expansion vessel, mixervalve			navitron	818
		210l store, no coils	1500x450, 75mm ins, 3 diffusers, 7 ports			newark	341.831					tim quote
		123l store, no coils	1050*400, 75mm ins, 3 diffusers, 7 ports			newark	266.831
		210l store, no coils	1500*450, 75mmins, 5sensor,10boss			newark	534.3665
		210l store, solar coil	1500*450, 75mmins, 5sensor,10boss			newark	618.32025
		210l store, boiler coil	1500*450, 75mmins, 5sensor,7boss			newark	589.69725

DHW		PHE	100kW			DPS	76.375
		Flow switch				DPS	35.25
		Pump	45W, DAB VA55/130			bes	30.08					13926
		TMV, 22mm	40l @1bar			hav	47.32					HEAT219058	RWC UFH	http://www.hav.co.uk/products/shw-detail.asp?pid=12917&cid=996	http://www.rwc.co.uk/Public/tmv/22mmUFH.pdf
		TMV, 22mm				Navitron	39
		Expansion tank	8l			BES	18.941					11350
		TMV, 22mm	20l @1bar			ebay	25						Triton

		Boilers - open vent
		Veissman Vitodens 100	18kW			inspired heating	714.4					7179919	veissman	http://www.inspiredheating.co.uk/acatalog/VIESSMANN_CONDENSING_BOILERS.html
		Flue				inspired heating	58.75					7184319	veissman	http://www.inspiredheating.co.uk/acatalog/VIESSMANN_CONDENSING_BOILERS.html
		Veissman Vitodens 100	18kW			bhl	690.9					7179920		http://www.bhl.co.uk/product/VMAN_VDENS100_24HE_OV_BLR_WB1A102_9919
		Flue				bhl	52.88					7184319	veissman	http://www.bhl.co.uk/product.php?productid=7229&page=1
		Bruderus 600	11KW			inspired heating	639.4						bruderus	http://www.inspiredheating.co.uk/acatalog/BUDERUS_600_REGULAR_RANGE_CONDENSING_BOILERS.html
		Flue				inspired heating	58.75					T000083702 / 7716191106	bruderus
		Atmos interopen HE22	22KW				635.9805						atmos	http://www.tbsmerchants.co.uk/cgi-bin/build/product/PGAT.html
		Flue
		Vaillant Ecotex 415	15Kw

		Veissmann Vitodens 200 Combi					875.61
		Veissmann Vitodens 100 Combi					807.23
		Flue					45
		Vaillant
		Atmos intercombi
Controls		Flowmeter	Digital, for solar loop			flowmeters.co.uk	39						email

		22mm compression elbow				b.e.s	1.60975					17687
		22mm compression tee				b.e.s	2.19725					17661
		pump isolating ball valves				b.e.s	2.78475					8132

		Y-pattern strainer				b.e.s	9.81125

Pipe
		Copper 22mm	3m			b.e.s.	12.2435					10312
			2m			b.e.s.	12.145					10311
		Copper 15mm	3m			b.e.s.	6.12175
			3m			ridgeons	5.0055
			2m			b.e.s.	4.07725
			2m			ridgeons	3.337
		Hep20 15mm	50m			plumbworld	40.94							http://www.plumbworld.co.uk/298-0000

Rads
		Towel Rail 1800x600	White, curved, 756Watts			plumbworld	72.97

Flooring

cellecta hidek18
cellecta screedboard 20
cemwod cw2000				50l bag		backtoearth	29.244
lithowood boards						backtoearth
Uditop woodfibre						backtoearth

## orders
Plumbing orders
		ridgeons		£51.80	b.e.s		£52.99
item	number	code	price (ex)	cost	code	price (ex vat)
1"BSP parallel female tee	1	B161	£1.93	£1.93	6546	£2.38	£2.38
1"BSP parallel male to 22mm compression joiner	1	PX42	£1.47	£1.47	17637	£1.41	£1.41
1"BSP fibre washer	5			£0.00	2415	£0.11	£0.55
1"BSP male cap	1	B185	£0.95	£0.95	6595	£0.98	£0.98
1"BSP taper Hex nipple	1	B144	£1.01	£1.01	6584	£2.59	£2.59
1"BSP parallel running nipple	1			£0.00	6578	£1.92	£1.92
Boss White tub, 400g	1			£0.00	6878	£1.15	£1.15
Hawk White jointing paste, 400g	1		£1.98	£1.98			£0.00
1"BSP Stop cap	1	B147	£0.80	£0.80	6609	£0.69	£0.69
22mm copper tube, 3m	4		£2.86	£11.44	10312	£3.47	£13.89
15mm copper tube, 1m	12		£1.43	£17.16	10310	£1.74	£20.84	1.99999999999999
22mm yorkshire straight connector	8	YP21	£0.44	£3.52			£0.00
22mm yorkshire elbow	2	YPS12	£0.78	£1.56			£0.00
22mm compression connector	2	PX40	£1.24	£2.48	17590	£1.24	£2.48
22mm compression elbow	3	PX44	£1.48	£4.44	17687	£1.37	£4.11
Gas meter Flex connector 1" BS746 female swivel to 1" BSP male taper	1		£3.06	£3.06			£0.00

	quantity	code	ex	inc
UFH1	https://www.underfloorheating1.co.uk				572.772
6-way manifold	1		218.67	262.404	262.404
Pump	0	?	0	0	0
Control pack	1		92	110.4	110.4
pipe, 16x2mm, 100m	0		75	90	0
pipe, 16x2mm, 200m	1		140	168	168
pipe, 16x2mm, 300m	0		210	252	0
			0	0	0
actuators		?	0	0	0
adaptors 16x1.8mm	12		2.22	2.664	31.968
blanking blugs	0	?	0	0	0

UFHtradedirect	http://ufhtradedirect.co.uk				726.216
6-way manifold	1		169	202.8	202.8
Pump+control pack	1		159	190.8	190.8
pipe 16x2mm, 50m	0		40	48	0
pipe 16x2mm, 100m	0		75	90	0
pipe 16x2mm, 200m	1		145	174	174
pipe 16x2mm, 500m	0		345	414	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		5.95	7.14	128.52
spreaders 1000 x 395, 2 slots, 200mm spacing	0		4.5	5.4	0
actuators		?		0	0
monoblocco adaptors 16x2mm	12		2.09	2.508	30.096
blanking blugs	8		0.99	1.188	9.504

BES	http://bes.co.uk				=
6-way manifold	1		0	0	0
Pump+control pack	1		0	0	0
pipe 16x2mm, 50m	0		0	0	0
pipe 16x2mm, 100m	0		0	0	0
pipe 16x2mm, 200m	1		0	0	0
pipe 16x2mm, 500m	0		0	0	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		0	0	0
spreaders 1000 x 395, 2 slots, 200mm spacing	0		0	0	0
actuators			0	0	0
monoblocco adaptors 16x2mm	12		0	0	0
blanking blugs	8		0	0	0

UFH Supply	http://www.ufhsupply.com/cat
6-way manifold (Ivar, inc adaptors, air valves, flow gauge)	1		262.8	315.36	315.36
Pump+control pack	1		0	0	0
pipe 16x2mm, 50m	0		0	0	0
pipe 16x2mm, 100m	1		165	198	198
pipe 16x2mm, 200m			230	276	0
pipe 16x2mm, 500m	0		0	0	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		0	0	0
spreaders 1000 x 395, 2 slots, 200mm spacing	0		0	0	0
actuators			0	0	0
blanking blugs	8		0	0	0

Grundfos Alpha2L 15-50	1		98	117.6	117.6			Anchor pumps	http://www.anchorpumps.com/pump-shop/manufacturers/grundfos/grundfos-alpha/grundfos-alpha2l-15-50-a-rated-eup-ready-domestic-circulator-240v
6-port manifold	1			200	200			Ebay	http://cgi.ebay.co.uk/ws/eBayISAPI.dll?ViewItem&item=120862182704&fromMakeTrack=true&ssPageName=VIP:watchlink:top:en

## Pipe Sizing
Pipe Sizing calcs

Gas
Section	Length	Extra lengthdue to fittings	Effective length	Boiler power	Required Gas flow rate	Pipe size	max length allowed	pressure loss	Progresive pressure loss	Notes
	m	m	m		m3/h	mm	m	mbar	mbar
Boiler	10.8	2	12.8	18	1.68	15	7	1.83	1.83	Too small
Boiler	10.8	2	12.8	18	1.68	22	30	0.43	0.43	OK
Boiler	10.8	2	12.8	27	2.52	22	26	0.49	0.49	OK

				Length of pipe (m)
			pipesize(mm)	3	6	9	12	15	20	25	30
			10	0.86	0.57	0.5	0.37	0.3	0.22	0.18	0.15
			12	1.5	1	0.85	0.82	0.69	0.52	0.41	0.34
			15	2.9	1.9	1.5	1.3	1.1	0.95	0.92	0.88
			22	8.7	5.8	4.6	3.9	3.4	2.9	2.5	2.3
			28	18	12	9.4	8	7	5.9	5.2	4.7

Water
Section	Length	Extra length due to fittings	Effective length	Boiler power	Required flow @20C delta	Pipe size		pressure loss		Notes
	m		m	kW	l/m	mm
Boiler loop	13	0.5	13.5	18	12.9	15
				8	5.7	15

section		heat transmission	temp diff	specific heat	flow rate	flow rate	pipe size	pressure loss	effective length	pressure needed
		kW	C	kJ/kgC	l/s	l/m	mm	Pa/m	m	Pa
boiler loop		18	20	4.19	0.22	12.90	22	260	13	3380
		8	20	4.19	0.10	5.73	15	410	13	5330
Rads	Emiter size	+20% for pipes	temp diff	specific heat	flow rate	flow rate	pipe size	pressure loss	effective length	pressure needed
pipe section	W	W	C	kJ/kgC	l/s	l/m	mm	Pa/m	m	Pa
A
B
C
D
E
F

solar loop
		2	14.3	4.186	0.033	2	10	300	13	3900
		0.2	2.9	4.186	0.017	1	10	180	13	2340
Optimal flow rates for diffusers/mantle:				0.15	0.2	0.15-0.2l/min/m2 ofpanel (Combisystem report)			0.435	0.9	l/min

		Flow Rate vs Pipe Size

		Flow rate (l/s)
Pressure loss		12mm	15mm	22mm	28mm	35mm	42mm	pipe size
90		0.021	0.04	0.118
92.5		0.022	0.041	0.12
95		0.022	0.042	0.122
97.5		0.022	0.042	0.124
100		0.023	0.043	0.125
120		0.025	0.047	0.139
140		0.028	0.052	0.152
160		0.03	0.056	0.164
180		0.032	0.06	0.175
200		0.034	0.064	0.186
220		0.036	0.067	0.196
240		0.038	0.071	0.206
260		0.039	0.074	0.215
280		0.041	0.077	0.224
300		0.043	0.08	0.233
320		0.044	0.083	0.242
340		0.046	0.086	0.25
360		0.048	0.089	0.258
380		0.049	0.092	0.266
400		0.05	0.094	0.274
420		0.052	0.097	0.282
440		0.053	0.099	0.289
460		0.055	0.102	0.297
480		0.056	0.104	0.304
500		0.057	0.107	0.311
520		0.059	0.109	0.318
540		0.06	0.112	0.324
560		0.061	0.114	0.331
580		0.061	0.116	0.338
600		0.064	0.119	0.344

## Flow rates
Pipe sizes/volumes
	dia	int dia	area	length	vol					Expansion vessel sizing
	(mm)	(mm2)	(mm)	(m)	(l)					Number of Tubes	47mm	58mm
copper	28	26.2	539	1	0.54					40	0
copper	22	20.2	320	1	0.32					Manifold volume (l)	2.4
copper	15	13.6	145	1	0.15					Pipe lengths	10mm	12mm	15mm	22mm
copper	12	11.3	100	1	0.10					12	0	1	0.2
copper	10	8.8	61	1	0.06					Pipe volume (l)	0.939216822902512
copper	8	6.8	36	1	0.04					Heat exchanger type	phe	(enter 'coil' or 'PHE')
Hep2O	22	18	254	1	0.25		guessed wall thickness				PHE dimensions(mm)		190	50	90
Hep20	15	11.8	109	1	0.11					PHE volume (l)		0.4275
Hep20	10	7.2	41	1	0.04					Coil volume (l)		1.8
					Heat Exchanger Volume(l)	0
		flowrate	Velocity					Total System volume (l)	3.33921682290251
		l/m	m/s
copper	22	19	0.99					Specific steam power at stagnation (W/m2)		30
	15	15	1.72					Pipe dissipation at stangation (W/m)		25
	12	6	1.00					Total stagnation input power (W)	84.6
	10	3.6	0.99					Pipe length containing steam (m)	1.692	(each side)
	8	2.2	1.01
Plastic	22	5	0.33					Steam vol (l)	2.60581905508952
	15	5	0.76					Liquid in exp vessel (l)	0
	10	5	2.05					PRV setting (bar)	3
					Height from EV to PRV (m)	1
					EV preset (bar)	1.3

					EV capacitance	0.190883190883191

					Expansion vessel min volume (l)	15.2257962354017

## panels
Panel efficiency/cost
			special	price	width	length	height	aperture	absorber	gross area	loss coef a2	loss coef a1	Conversion factor	area	power	manifold vol
			£	£	mm	mm	mm	m2	m2	m2	W/(m2K2)	W/(m2K2)		m2	kWh/m2	l
Navitron SFB20				395	1466	1639		1.75		2.25	0.004	1.61	0.561	1.41	626	0.9	761
economical 47-1500-20			256.15	319.6	1610	1700	140	1.26	1.15	2.74					1	650	0.85
economical 58-1800-20					1.90	1.61		0.0083	2.085	0.573
			0.65	0.81				1.28

				η(x) = η0 – a1 * x – a2 * x^2 * Gkwhere x = (Tm – Ta) / Gk
				Gk = irradiation (W)
				Ta(Ambient Temp)
				Tm(Collector temp)

## PHE Energy
Sums on PHE energy transfer
	sensorA	sensorB	sensorC
	solin	solout	solout2		soldiff	mismatch	soldiff2		sensorC placed next to solout
	42.1	40.3	37.06		1.8	3.24	5.04
	41.1	40.1	33.06		1	7.04	8.04
	40.5	39.5	36.5		1	3	4
	40.4	39.3	35.3		1.1	4	5.1
	39.7	38.6	34.2		1.1	4.4	5.5
	39.1	37.9	34		1.2	3.9	5.1
					3.825
	solin	solout	solin2					sensorC placed next to solin
	38.38	37.44	38.38		0.940000000000005	0	0.940000000000005
	38.3	37.3	37.69		1	0.609999999999999	0.609999999999999
	38.25	37	37.5		1.25	0.75	0.75
	38.3	36.44	37.375		1.86	0.924999999999997	0.924999999999997
	38.3	35.8	37.3		2.5	1	1
	38.06	35.25	37.19		2.81	0.870000000000005	0.870000000000005
	24.56	31.43	22.8			0.831

	conclusion: sensor C reads 3.8C lower than sensorB and 0.8C lower than sensorA

## 'file:///home/wookey/docs/DIY/heating/Househeating.xlsx'#DHW usage
6
11

## 'file:///home/wookey/docs/DIY/heating/Househeating.xlsx'#Monthly overview
4.5