## Sheet1
Expansion vessel sizing					Pipe sizes/volumes
Number of Tubes	47mm	58mm					dia	int dia	area	length	vol
	40	0					(mm)	(mm2)	(mm)	(m)	(l)
Manifold volume (l)	2.4					copper	28	26.2	539.128715282544	1	0.54
Pipe lengths	10mm	12mm	15mm	22mm			copper	22	20.2	320.473866592695	1	0.32
	8	0	1	0			copper	15	13.6	145.267244301992	1	0.15
Pipe volume (l)	0.6					copper	12	11.3	100.28749148422	1	0.10
Heat exchanger type	PHE	(enter 'coil' or 'PHE')					copper	10	8.8	60.8212337734984	1	0.06
PHE dimensions(mm)		190	50	90			copper	8	6.8	36.316811075498	1	0.04
PHE volume (l)		0.4
Coil volume (l)		1.8
Heat Exchanger Volume(l)	0.4
Total System volume (l)	3.5

System fill pressure (bar)		1.5	(1-2.5, typical)				Insulation	W/mK
Specific steam power at stagnation (W/m2)	79.5	(constants from Hausner & Fink, fig3)					Armaflex HT	0.036
Insulation thickness(mm)		13
Pipe Diameter near panel(mm)		10
Pipe dissipation at stagnation (W/m)	25	(from Hausner & Fink)
Total stagnation input power (W)	254.4
Pipe length containing steam (m)	5.1	(each side)

Steam vol (l)	3.1
Liquid in exp vessel (l)	0.5
PRV setting (bar)	3.5
Height from EV to PRV (m)	0
EV preset (bar)	1.2

EV capacitance	0.30

Expansion vessel min volume (l)	13.0

## Regression (1)
SUMMARY OUTPUT

Regression Statistics
Multiple R	-0.9989061072387
R Square	0.9978134110787
Adjusted R Square	0.9956268221574
Standard Error	1.2247448713916
Observations	3

ANOVA
	df	SS	MS	F	Significance of F
Regression	1	684.5	684.5	456.333333333341	0.0297798216377
Residual	1	1.5	1.5
Total	2	686

	Coefficients	Standard Error	t Stat	P-value	Lower 95%	Upper 95%
Intercept	120.071428571428	3.1727474735018	37.8446219165697	0.0168180215709	79.7578495969332	160.385007545923
Column 1	-26.4285714285713	1.2371791482635	-21.3619599600161	0.0297798216377	-42.1484229817333	-10.7087198754093